## Lighting System
Lamp Type | Lumen | Rating | Company | Cost
Metal Halide | 14100 | 250 |  |  |  | Lighting loss factor | 0.9
High Pressur | 26100 | 250
CFL | 800 | 15 | GE |  |  | Number of Lamps per Luminaire | 1
| 1100 | 20 | GE | 2.41
| 1750 | 26 | GE | 3.13
LED | 800 | 13 | GE | 1.57
Incadescent Blub | 490 | 40
Tube Light | 750 | 39
Sr.No. | Room Name | length Ft | Width Ft | Height ft | Light Ceiling m | Working Hight Floor m | HM m | Room Index RI | Utilization factor | Standard Requirment | Lights Used | Number of Lights Required
1 | STP 1 to 12 | 20 | 20 | 20 | 2 | 0 | 4.1538 | 12.7811 | 0.34 | 80 | MH | 0.70217
2 | STP 13 to 18 | 28.6 | 21.1 | 11 | 0 | 0 | 3.3846 | 12.645 | 0.34 | 80 | MH | 1.0593
3 | Meter Room | 10 | 10 | 10 | 0.3 | 0 | 2.7769 | 4.2722 | 0.32 | 240 | CFL15 | 9.8619
4 | Society Office | 10 | 10 | 10 | 0.3 | 0 | 2.7769 | 4.2722 | 0.32 | 240 | CFL15 | 7.1723
5 | STP 19 to 20 | 10 | 10 | 11 | 0 | 0 | 3.3846 | 5.2071 | 0.34 | 80 | MH | 0.17554
6 | Entrance Loobby | 14 | 10 | 11 | 0 | 0 | 3.3846 | 6.075 | 0.34 | 160 | CFL15 | 6.3004
7 | Meter Room | 7.9 | 8 | 11 | 0.3 | 0 | 3.0846 | 3.7726 | 0.32 | 240 | CFL15 | 4.5329
8 | STP 21 to 24 | 27.6 | 12.5 | 11 | 0 | 0 | 3.3846 | 8.9598 | 0.34 | 80 | MH | 0.60562
9 | STP 25 &26 | 8 | 15.1 | 11 | 0 | 0 | 3.3846 | 5.446 | 0.34 | 80 | MH | 0.21206
10 | STP 27&28 | 9.9 | 17 | 11 | 0 | 0 | 3.3846 | 6.5157 | 0.34 | 80 | MH | 0.29544
11 | Entrance Loobby | 10 | 14.6 | 11 | 0.3 | 0 | 3.0846 | 5.6329 | 0.34 | 160 | CFL15 | 6.5704
12 | Meter Room | 7 | 9 | 11 | 0.3 | 0 | 3.0846 | 3.7371 | 0.32 | 240 | CFL15 | 4.5186
13 | Service Room | 6.6 | 4 | 11 | 0.3 | 0 | 3.0846 | 2.3638 | 0.3 | 160 | CFL15 | 1.3465
14 | STP 19 &30 | 9 | 13.8 | 11 | 0 | 0 | 3.3846 | 5.673 | 0.34 | 80 | MH | 0.21802
15 | Stair Case-1 | 12 | 18.4 | 0 | 0 | 0 | 0 | 0 | 0.18 | 80 | LED13 | 12.9038
16 | Stair Case-2 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0.18 | 80 | LED13 | 5.8441

## Ventilation Requriments
The Building Material generates pollution
The Building Material generates pollution | 0.7 | olf/m2 | Avg Person | 5 | olf | Heavy Smoker | 20 | olf
PD | 5 | % |  |  |  | Co | 0.2
| 20 | %
Recommended air supply rate l/sec | Avg persons | 5
| Loobby | 8
Per m2 area |  | 3
Sr.No. | Room Name | length Ft | Width Ft | Height ft | length m | Width m | Height m | Volume m3 | Area m2 | Number of Occupants | Air requriments | Number of Air Changes | Blower/Fan Required | Total Human Pollution | Pollution Due to Building material | G | Ci | V liters/sec | Number of Air Changes
1 | STP 1 to 12 | 20 | 10 | 10 | 6.1538 | 3.0769 | 3.0769 | 58.2613 | 18.9349 | 12 | 60 | 1.0298 | 0.063566 | 240 | 13.2544 | 253.2544 | 0.30695 | x` | #VALUE!
2 | STP 13 to 18 | 10 | 10 | 10 | 3.0769 | 3.0769 | 3.0769 | 29.1306 | 9.4675 | 6 | 30 | 1.0298 | 0.031783 | 120 | 6.6272 | 126.6272 | 0.30695 | 11839.7576 | 406.4367
3 | Meter Room | 7.8 | 8.6 | 11 | 2.4 | 2.6462 | 3.3846 | 21.4949 | 6.3508 | 2 | 16 | 0.74436 | 0.016951 | 40 | 4.4455 | 44.4455 | 1.4121 | 366.6807 | 17.059
4 | Society Office | 6.6 | 9 | 11 | 2.0308 | 2.7692 | 3.3846 | 19.034 | 5.6237 | 10 | 80 | 4.203 | 0.084755 | 200 | 3.9366 | 203.9366 | 1.4121 | 1682.4996 | 88.3946
5 | STP 19 to 20 | 10 | 12.4 | 11 | 3.0769 | 3.8154 | 3.3846 | 39.7342 | 11.7396 | 2 | 10 | 0.25167 | 0.010594 | 40 | 8.2178 | 48.2178 | 0.30695 | 4508.4027 | 113.4641
6 | Entrance Loobby | 14 | 10 | 11 | 4.3077 | 3.0769 | 3.3846 | 44.8612 | 13.2544 | 0 | 39.7633 | 0.88636 | 0.042127 | 0 | 9.2781 | 9.2781 | 1.4121 | 76.5454 | 1.7063
7 | Meter Room | 7.9 | 8 | 11 | 2.4308 | 2.4615 | 3.3846 | 20.2516 | 5.9834 | 4 | 20 | 0.98758 | 0.021189 | 80 | 4.1884 | 84.1884 | 1.4121 | 694.5638 | 34.2967
8 | STP 21 to 24 | 27.6 | 12.5 | 11 | 8.4923 | 3.8462 | 3.3846 | 110.5508 | 32.6627 | 2 | 10 | 0.090456 | 0.010594 | 40 | 22.8639 | 62.8639 | 0.30695 | 5877.8311 | 53.1686
9 | STP 25 &26 | 8 | 15.1 | 11 | 2.4615 | 4.6462 | 3.3846 | 38.7088 | 11.4367 | 2 | 10 | 0.25834 | 0.010594 | 40 | 8.0057 | 48.0057 | 0.30695 | 4488.5738 | 115.9575
10 | STP 27&28 | 9.9 | 17 | 11 | 3.0462 | 5.2308 | 3.3846 | 53.9295 | 15.9337 | 2 | 10 | 0.18543 | 0.010594 | 40 | 11.1536 | 51.1536 | 0.30695 | 4782.908 | 88.6881
11 | Entrance Loobby | 10 | 14.6 | 11 | 3.0769 | 4.4923 | 3.3846 | 46.7838 | 13.8225 | 0 | 41.4675 | 0.88636 | 0.043932 | 0 | 9.6757 | 9.6757 | 1.4121 | 79.8259 | 1.7063
12 | Meter Room | 7 | 9 | 11 | 2.1538 | 2.7692 | 3.3846 | 20.1875 | 5.9645 | 2 | 10 | 0.49536 | 0.010594 | 40 | 4.1751 | 44.1751 | 1.4121 | 364.4499 | 18.0532
13 | Service Room | 6.6 | 4 | 11 | 2.0308 | 1.2308 | 3.3846 | 8.4595 | 2.4994 | 3 | 15 | 1.7731 | 0.015892 | 60 | 1.7496 | 61.7496 | 1.4121 | 509.441 | 60.2209
14 | STP 19 &30 | 9 | 13.8 | 11 | 2.7692 | 4.2462 | 3.3846 | 39.7983 | 11.7586 | 2 | 10 | 0.25127 | 0.010594 | 40 | 8.231 | 48.231 | 0.30695 | 4509.642 | 113.3125
15 | Stair Case-1 | 12 | 18.4 | 0 | 3.6923 | 5.6615 | 0 | 0 | 20.9041 | 0 | 62.7124 |  |  | 0 | 14.6329 | 14.6329 | 1.4121 | 120.7231
16 | Stair Case-2 | 11.6 | 18.11 | 0 | 3.5692 | 5.5723 | 0 | 0 | 19.8889 | 0 | 59.6666 |  |  | 0 | 13.9222 | 13.9222 | 1.4121 | 114.8597
Standard CFM
Type of Fan | 2000
Bajaj | 7000
Crompton | 8000
Crompton | 6000
D
Conversion factor CFM to l/sec | 0.47195

## Heating or Cooling Load
Metabolic Rate of Common man with normal Activity |  | 120
Fresh air Circulation is |  | 0.3 | 30%
Inside Temperature |  | 25 | oC
Outside temperature |  | 35 | oC
Absolute Humidty outside |  | 0.013
Inside Humidity |  | 0.0075
Sr.No. | Room Name | length Ft | Width Ft | Height ft | length m | Width m | Height m | Volume m3 | Area m2 | Number of Occupants | Air requriments | Load due to occupants (w) | Number of Lights | Lights Used | Power Rating | Lighting Load (W) | Sensible Load due to fresh air Circulation W | Latent Heat Load on the System (kW) | Total Heating Load W
1 | STP 1 to 12 | 10 | 10 | 10 | 3.0769 | 3.0769 | 3.0769 | 29.1306 | 9.4675 | 12 | 60 | 1440 | 2 | MH | 250 | 500 | 233.4794 | 273.9411 | 2447.4206
2 | STP 13 to 18 | 28.6 | 21.1 | 11 | 8.8 | 6.4923 | 3.3846 | 193.3709 | 57.1323 | 6 | 30 | 720 | 1.0593 | MH | 250 | 264.8325 | 116.7397 | 136.9706 | 1238.5427
3 | Meter Room | 7.8 | 8.6 | 11 | 2.4 | 2.6462 | 3.3846 | 21.4949 | 6.3508 | 2 | 16 | 240 | 6.6154 | CFL15 | 15 | 99.2308 | 62.2612 | 73.051 | 474.5429
4 | Society Office | 6.6 | 9 | 11 | 2.0308 | 2.7692 | 3.3846 | 19.034 | 5.6237 | 10 | 80 | 1200 | 4.2604 | CFL15 | 15 | 63.9053 | 311.3059 | 365.2548 | 1940.4661
5 | STP 19 to 20 | 10 | 12.4 | 11 | 3.0769 | 3.8154 | 3.3846 | 39.7342 | 11.7396 | 2 | 10 | 240 | 0.21767 | MH | 250 | 54.4182 | 38.9132 | 45.6569 | 378.9883
6 | Entrance Loobby | 14 | 10 | 11 | 4.3077 | 3.0769 | 3.3846 | 44.8612 | 13.2544 | 0 | 39.7633 | 0 | 6.3004 | CFL15 | 15 | 94.5058 | 154.7319 | 181.5468 | 430.7845
7 | Meter Room | 7.9 | 8 | 11 | 2.4308 | 2.4615 | 3.3846 | 20.2516 | 5.9834 | 4 | 20 | 480 | 4.5329 | CFL15 | 15 | 67.9935 | 77.8265 | 91.3137 | 717.1337
8 | STP 21 to 24 | 27.6 | 12.5 | 11 | 8.4923 | 3.8462 | 3.3846 | 110.5508 | 32.6627 | 2 | 10 | 240 | 0.60562 | MH | 250 | 151.4056 | 38.9132 | 45.6569 | 475.9757
9 | STP 25 &26 | 8 | 15.1 | 11 | 2.4615 | 4.6462 | 3.3846 | 38.7088 | 11.4367 | 2 | 10 | 240 | 0.21206 | MH | 250 | 53.0139 | 38.9132 | 45.6569 | 377.584
10 | STP 27&28 | 9.9 | 17 | 11 | 3.0462 | 5.2308 | 3.3846 | 53.9295 | 15.9337 | 2 | 10 | 240 | 0.29544 | MH | 250 | 73.8596 | 38.9132 | 45.6569 | 398.4297
11 | Entrance Loobby | 10 | 14.6 | 11 | 3.0769 | 4.4923 | 3.3846 | 46.7838 | 13.8225 | 0 | 41.4675 | 0 | 6.5704 | CFL15 | 15 | 98.556 | 161.3633 | 189.3274 | 449.2467
12 | Meter Room | 7 | 9 | 11 | 2.1538 | 2.7692 | 3.3846 | 20.1875 | 5.9645 | 2 | 10 | 240 | 4.5186 | CFL15 | 15 | 67.7784 | 38.9132 | 45.6569 | 392.3485
13 | Service Room | 6.6 | 4 | 11 | 2.0308 | 1.2308 | 3.3846 | 8.4595 | 2.4994 | 3 | 15 | 360 | 1.3465 | CFL15 | 15 | 20.1972 | 58.3699 | 68.4853 | 507.0524
14 | STP 19 &30 | 9 | 13.8 | 11 | 2.7692 | 4.2462 | 3.3846 | 39.7983 | 11.7586 | 2 | 10 | 240 | 0.21802 | MH | 250 | 54.506 | 38.9132 | 45.6569 | 379.0761
15 | Stair Case-1 | 12 | 18.4 | 0 | 3.6923 | 5.6615 | 0 | 0 | 20.9041 | 0 | 62.7124 | 0 | 12.9038 | LED13 | 13 | 167.7493 | 244.0344 | 286.3252 | 698.1089
16 | Stair Case-2 | 11.6 | 18.11 | 0 | 3.5692 | 5.5723 | 0 | 0 | 19.8889 | 0 | 59.6666 | 0 | 12.2771 | LED13 | 13 | 159.6019 | 232.1819 | 272.4187 | 664.2025
[19 empty] | 11969.9032 | Watts
[19 empty] | 11.9699 | kW
[19 empty] | 3.42 | TR
1 | Auditorium | 130 | 81 | 25 | 40 | 24.9231 | 7.6923 | 7668.6391 | 996.9231 | 450 | 3375 | 54000 | 1.9464 | MH | 250 | 486.6043 | 13133.2185 | 15409.1879 | 83029.0107 | Auditorium
[19 empty] | 83.029 | kW
[11 empty] | 1.4062 | [7 empty] | 23.7226 | TR

## Solar Gain
Inside Temperature |  | 25 | oC
Outside temperature |  | 35 | oC
Absolute Humidty outside |  | 0.013 | kg/kg
Inside Humidity |  | 0.0075 | kg/kg
U Wall |  | 0.7 | W/m2oC
U for Windows |  | 5.6 | W/m2oC
Solar Insolation |  | 150 | W/m2
Fs for Window | 0.51 | lightly heat absorbing glass
60.52
Sr.No. | Room Name | length Ft | Height ft | length m | Height m | Area m2 | Solar load W
1 | Walls with widows | 10 | 10 | 3.0769 | 3.0769 | 9.4675
2 | Windows | 2 | 3 | 0.61538 | 0.92308 | 0.56805 | 477.1598
3 | walls excluding windows | 8 | 7 | 2.4615 | 2.1538 | 5.3018 | 37.1124
514.2722
[7 empty] | 0.51427 | kW
[7 empty] | 0.14693 | TR
0.30769
0.30769